## bus
| name | vn_kv | type | zone | in_service | description | substat | folder_id | sernum | for_name | chr_name
22401 | ElmTerm22402 | 21 | b | example_grid | TRUE |  |  | SWF
22402 | 7097097_001001_000000_00010001_02001 | 0.4 | b | example_grid | TRUE |  |  | SWF
22548 | 7097097_001001_001001_00050007_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF
22549 | 7097097_001001_001001_00070007_03001 | 0.4 | m | example_grid | TRUE |  |  | SWF
29590 | 7097097_001001_001001_00260026_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF
15385 | 7097097_001001_001001_00220022_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF |  | 61AAEA8A497D437AB30685224FBB9EE0
19999 | 7097097_001001_001001_00030003_01002 | 0.4 | m | example_grid | TRUE |  |  | SWF |  | 4AE799ED14704D7AB781BC4572DF188E
22562 | 7097097_001001_001001_00140016_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF
19880 | 7097097_001001_001001_00040004_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF |  | 59971D2913A24FCA89BD0D24C9141A05
22056 | 7097097_001001_001001_00100010_03001 | 0.4 | m | example_grid | TRUE |  |  | SWF
22572 | 7097097_001001_001001_00090009_03001 | 0.4 | m | example_grid | TRUE |  |  | SWF
22573 | 7097097_001001_001001_00180021_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF
23736 | 7097097_001001_001001_00020003_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF
21819 | 7097097_001001_001001_00020002_03001 | 0.4 | m | example_grid | TRUE |  |  | SWF
14276 | 7097097_001001_001001_00060006_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF |  | 6D223B78050B46FAA8729EFFE1D25604
22092 | 7097097_001001_001001_00120012_03001 | 0.4 | m | example_grid | TRUE |  |  | SWF
25805 | 7097097_001001_001001_00050005_03001 | 0.4 | m | example_grid | TRUE |  |  | SWF
22097 | 7097097_001001_001001_00080008_03001 | 0.4 | m | example_grid | TRUE |  |  | SWF
17618 | 7097097_001001_001001_00230023_01002 | 0.4 | m | example_grid | TRUE |  |  | SWF |  | 0260198CA2EA4C4BB15BA2258ACDB571
22102 | 7097097_001001_001001_00180018_03001 | 0.4 | m | example_grid | TRUE |  |  | SWF
20571 | 7097097_001001_001001_00150015_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF |  | 7E05E31F30A34212955D407722CA8288
22109 | 7097097_001001_001001_00140014_03001 | 0.4 | m | example_grid | TRUE |  |  | SWF
17379 | 7097097_001001_001001_00130013_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF |  | 1B36190F56E64ADEA788E8CD1F4B3A11
13674 | 7097097_001001_001001_00110011_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF |  | 4621B2EA9FFE4E22900F3D6B2F9EBADD
17645 | 7097097_001001_001001_00170017_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF |  | 13ECFA6780064CC6B010005EA7734D73
18541 | 7097097_001001_001001_00250025_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF |  | FC2232F0D2E348778733489E804AC662
20593 | 7097097_001001_001001_00190019_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF |  | B1123280E5DC414B980D8BE284CC6103
33266 | 7097097_001001_001001_00010002_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF
15603 | 7097097_001001_001001_00210021_01002 | 0.4 | m | example_grid | TRUE |  |  | SWF |  | 71621AAC1AC541B091A67179F30DD712
29044 | 7097097_001001_001001_00240024_03001 | 0.4 | m | example_grid | TRUE |  |  | SWF
25593 | 7097097_001001_001001_00200023_01001 | 0.4 | m | example_grid | TRUE |  |  | SWF
25594 | 7097097_001001_001001_00200020_03001 | 0.4 | m | example_grid | TRUE |  |  | SWF
17531 | 7097097_001001_001001_00160016_01002 | 0.4 | m | example_grid | TRUE |  |  | SWF |  | 2546F85F68E64E5CB2523161FE0117D3

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type | description | sernum | for_name | chr_name
0 |  | 13674 | 93.9155 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:93.916,file:000024130.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
1 |  | 13674 | 1.3465 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:0,demand:1.34652,file_add:000024131.csv,file:NaN,load_type:heat,temperature:55
2 |  | 13674 | 0.0385 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:0,demand:0.0385,file_add:000024132.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.077
3 |  | 15385 | 77.7387 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:77.739,file:000024137.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
4 |  | 15385 | 0.29536 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:3,demand:0.29536,file_add:000024138.csv,file:NaN,load_type:heat,temperature:55
5 |  | 15385 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:3,demand:0.011,file:NaN,file_add:000024139.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
6 |  | 15385 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:3,demand:0.011,file:NaN,file_add:000024140.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
7 |  | 15385 | 0.0076 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:3,demand:0.0076,file_add:000024141.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0152
8 |  | 15603 | 140.6927 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:140.693,file:000024143.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
9 |  | 15603 | 0.889 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:8,demand:0.889,file_add:000024144.csv,file:NaN,load_type:heat,temperature:55
10 |  | 15603 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:8,demand:0.011,file:NaN,file_add:000024145.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
11 |  | 15603 | 0.0146 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:8,demand:0.0146,file_add:000024146.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0292
12 |  | 17379 | 96.3585 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:96.358,file:000024148.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
13 |  | 17379 | 0.88148 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:12,demand:0.88148,file_add:000024149.csv,file:NaN,load_type:heat,temperature:55
14 |  | 17379 | 0.0147 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:12,demand:0.0147,file_add:000024150.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0294
15 |  | 17531 | 140.6927 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:140.693,file:000024153.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
16 |  | 17531 | 0.33044 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:15,demand:0.33044,file_add:000024154.csv,file:NaN,load_type:heat,temperature:55
17 |  | 17531 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:15,demand:0.011,file:NaN,file_add:000024155.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
18 |  | 17531 | 0.0069 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:15,demand:0.0069,file_add:000024156.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0138
19 |  | 17618 | 226.7572 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:226.757,file:000024158.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
20 |  | 17618 | 0.29244 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:19,demand:0.29244,file_add:000024159.csv,file:NaN,load_type:heat,temperature:55
21 |  | 17618 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:19,demand:0.011,file:NaN,file_add:000024160.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
22 |  | 17618 | 0.0074 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:19,demand:0.0074,file_add:000024161.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0148
23 |  | 17645 | 41.9905 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:41.99,file:000024163.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
24 |  | 17645 | 1.4031 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:23,demand:1.4031200000000001,file_add:000024164.csv,file:NaN,load_type:heat,temperature:55
25 |  | 17645 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:23,demand:0.011,file:NaN,file_add:000024165.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
26 |  | 17645 | 0.014 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:23,demand:0.014,file_add:000024166.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.028
27 |  | 18541 | 140.6927 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:140.693,file:000024169.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
28 |  | 18541 | 2.592 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:27,demand:2.59196,file_add:000024170.csv,file:NaN,load_type:heat,temperature:55
29 |  | 18541 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:27,demand:0.011,file:NaN,file_add:000024171.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
30 |  | 18541 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:27,demand:0.011,file:NaN,file_add:000024172.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
31 |  | 18541 | 0.0289 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:27,demand:0.0289,file_add:000024173.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0578
32 |  | 19880 | 504.5752 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:504.575,file:000024177.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
33 |  | 20571 | 226.7572 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:226.757,file:000024178.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
34 |  | 20571 | 1.0237 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:33,demand:1.0236800000000001,file_add:000024179.csv,file:NaN,load_type:heat,temperature:55
35 |  | 20571 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:33,demand:0.011,file:NaN,file_add:000024180.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
36 |  | 20571 | 0.0135 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:33,demand:0.0135,file_add:000024181.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.027
37 |  | 20593 | 169.5213 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:169.521,file:000024186.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
38 |  | 20593 | 0.4912 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:37,demand:0.4912,file_add:000024187.csv,file:NaN,load_type:heat,temperature:55
39 |  | 20593 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:37,demand:0.011,file:NaN,file_add:000024188.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
40 |  | 20593 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:37,demand:0.011,file:NaN,file_add:000024189.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
41 |  | 20593 | 0.0075 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:37,demand:0.0075,file_add:000024190.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.015

## sgen
| name | bus | p_mw | q_mvar | sn_mva | scaling | in_service | type | current_source | description
0 |  | 13674 | 0.0051 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:0,power:0.0051,file:000024133.csv,cos_phi:0.95,orientation:124,angle:60
1 |  | 13674 | 0.0112 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:0,power:0.0112,file:000024134.csv,cos_phi:0.95,orientation:214,angle:52
2 |  | 13674 | 0.0051 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:0,power:0.0051,file:000024135.csv,cos_phi:0.95,orientation:304,angle:60
3 |  | 13674 | 0.0057 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:0,power:0.0057,file:000024136.csv,cos_phi:0.95,orientation:304,angle:75
4 |  | 13674 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:0,power:0.0271,file:NaN,cos_phi:1,capacity:0.0271,efficiency:0.99,soc:0.5,g2b:True,b2g:True
5 |  | 13674 | 0.8031 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:0,power:0.1155,capacity:0.154,efficiency:0.99,soc:0.5
6 |  | 15385 | 0.0102 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:3,power:0.0102,file:000024142.csv,cos_phi:0.95,orientation:183,angle:37
7 |  | 15385 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:3,power:0.0102,file:NaN,cos_phi:1,capacity:0.0102,efficiency:0.99,soc:0.5,g2b:True,b2g:True
8 |  | 15385 | 0.2345 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:3,power:0.0228,capacity:0.0304,efficiency:0.99,soc:0.5
9 |  | 15603 | 0.0122 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:8,power:0.0122,file:000024147.csv,cos_phi:0.95,orientation:182,angle:39
10 |  | 15603 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:8,power:0.0122,file:NaN,cos_phi:1,capacity:0.0122,efficiency:0.99,soc:0.5,g2b:True,b2g:True
11 |  | 15603 | 0.2473 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:8,power:0.0438,capacity:0.0584,efficiency:0.99,soc:0.5
12 |  | 17379 | 0.0127 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:12,power:0.0127,file:000024151.csv,cos_phi:0.95,orientation:100,angle:38
13 |  | 17379 | 0.0138 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:12,power:0.0138,file:000024152.csv,cos_phi:0.95,orientation:280,angle:38
14 |  | 17379 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:12,power:0.0265,file:NaN,cos_phi:1,capacity:0.0265,efficiency:0.99,soc:0.5,g2b:True,b2g:True
15 |  | 17379 | 0.6352 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:12,power:0.0441,capacity:0.0588,efficiency:0.99,soc:0.5
16 |  | 17531 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:15,power:0.0092,file:NaN,cos_phi:1,capacity:0.0092,efficiency:0.99,soc:0.5,g2b:True,b2g:True
17 |  | 17531 | 0.1224 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:15,power:0.0207,capacity:0.0276,efficiency:0.99,soc:0.5
18 |  | 17618 | 0.0087 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:19,power:0.0087,file:000024162.csv,cos_phi:0.95,orientation:188,angle:44
19 |  | 17618 | 0.1122 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:19,power:0.0222,capacity:0.0296,efficiency:0.99,soc:0.5
20 |  | 17645 | 0.0234 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:23,power:0.0234,file:000024167.csv,cos_phi:0.95,orientation:275,angle:39
21 |  | 17645 | 0.0005 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:23,power:0.0005,file:000024168.csv,cos_phi:0.95,orientation:95,angle:54
22 |  | 17645 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:23,power:0.0239,file:NaN,cos_phi:1,capacity:0.0239,efficiency:0.99,soc:0.5,g2b:True,b2g:True
23 |  | 17645 | 0.4385 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:23,power:0.042,capacity:0.056,efficiency:0.99,soc:0.5
24 |  | 18541 | 0.0194 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:27,power:0.0194,file:000024174.csv,cos_phi:0.95,orientation:129,angle:47
25 |  | 18541 | 0.0114 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:27,power:0.0114,file:000024175.csv,cos_phi:0.95,orientation:224,angle:47
26 |  | 18541 | 0.014 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:27,power:0.014,file:000024176.csv,cos_phi:0.95,orientation:309,angle:47
27 |  | 18541 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:27,power:0.0448,file:NaN,cos_phi:1,capacity:0.0448,efficiency:0.99,soc:0.5,g2b:True,b2g:True
28 |  | 18541 | 1.0651 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:27,power:0.0867,capacity:0.1156,efficiency:0.99,soc:0.5
29 |  | 20571 | 0.0054 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:33,power:0.0054,file:000024182.csv,cos_phi:0.95,orientation:173,angle:46
30 |  | 20571 | 0.0134 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:33,power:0.0134,file:000024183.csv,cos_phi:0.95,orientation:263,angle:50
31 |  | 20571 | 0.0001 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:33,power:0.0001,file:000024184.csv,cos_phi:0.95,orientation:353,angle:61
32 |  | 20571 | 0.004 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:33,power:0.004,file:000024185.csv,cos_phi:0.95,orientation:83,angle:61
33 |  | 20571 | 0.384 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:33,power:0.0405,capacity:0.054,efficiency:0.99,soc:0.5
34 |  | 20593 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:37,power:0.0108,file:NaN,cos_phi:1,capacity:0.0108,efficiency:0.99,soc:0.5,g2b:True,b2g:True
35 |  | 20593 | 0.0811 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:37,power:0.0225,capacity:0.03,efficiency:0.99,soc:0.5

## switch
| bus | element | et | type | closed | name | z_ohm | in_ka
1258 | 21819 | 29617 | l | CB | TRUE |  | 0
2457 | 22402 | 33964 | l | CB | TRUE |  | 0

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service | s_sc_max_mva | s_sc_min_mva | rx_min | rx_max | r0x0_max | x0x_max | r0x0_min | x0x_min | description
1 | 5000000_000000_000000_00000000_04002 | 22401 | 1 | 0 | 1 | TRUE | 10000 | 8000 | 0.1 | 0.1 | 0.1 | 1 | 0.1 | 1
2 | 3097097_000139 | 22401 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service | r0_ohm_per_km | x0_ohm_per_km | c0_nf_per_km | alpha | temperature_degree_celsius | description | line_idx | folder_id | section_idx
12841 | 7097097_001001_001001_00050007_06002 | 24-AL1/4-ST1A 0.4_air | 22548 | 22549 | 0.053 | 1.2012 | 0.335 | 11.25 | 0 | 0.31 | 1 | 1 | ol | TRUE | 0 | 0 | 0 | 0.00403 | 90 |  | 12841 | SWF | 0
12846 | 7097097_001001_001001_00120014_06001 | 94-AL1/15-ST1A 0.4_air | 22092 | 22109 | 0.024 | 0.306 | 0.29 | 13.2 | 0 | 0.31 | 1 | 1 | ol | TRUE | 0 | 0 | 0 | 0.00403 | 90 |  | 12846 | SWF | 0
12865 | 7097097_001001_001001_00070008_06001 | 70-AL1/11-ST1A_air | 22549 | 22097 | 0.086 | 0.413 | 0.29 | 12.6 | 0 | 0.31 | 1 | 1 | ol | TRUE | 0 | 0 | 0 | 0.00403 | 90 |  | 12865 | SWF | 0
12866 | 7097097_001001_001001_00080010_06001 | 70-AL1/11-ST1A_air | 22097 | 22056 | 0.054 | 0.413 | 0.29 | 12.6 | 0 | 0.31 | 1 | 1 | ol | TRUE | 0 | 0 | 0 | 0.00403 | 90 |  | 12866 | SWF | 0
12867 | 7097097_001001_001001_00100012_06001 | 70-AL1/11-ST1A_air | 22056 | 22092 | 0.019 | 0.413 | 0.29 | 12.6 | 0 | 0.31 | 1 | 1 | ol | TRUE | 0 | 0 | 0 | 0.00403 | 90 |  | 12867 | SWF | 0
12870 | 7097097_001001_001001_00140016_06001 | 24-AL1/4-ST1A 0.4_air | 22562 | 22109 | 0.047 | 1.2012 | 0.335 | 11.25 | 0 | 0.31 | 1 | 1 | ol | TRUE | 0 | 0 | 0 | 0.00403 | 90 |  | 12870 | SWF | 0
12893 | 7097097_001001_001001_00070009_06001 | 48-AL1/8-ST1A 0.4_air | 22549 | 22572 | 0.029 | 0.5939 | 0.3 | 12.2 | 0 | 0.31 | 1 | 1 | ol | TRUE | 0 | 0 | 0 | 0.00403 | 90 |  | 12893 | SWF | 0
12894 | 7097097_001001_001001_00090018_06001 | 48-AL1/8-ST1A 0.4_air | 22572 | 22102 | 0.037 | 0.5939 | 0.3 | 12.2 | 0 | 0.31 | 1 | 1 | ol | TRUE | 0 | 0 | 0 | 0.00403 | 90 |  | 12894 | SWF | 0
12895 | 7097097_001001_001001_00180021_06001 | 48-AL1/8-ST1A 0.4_air | 22102 | 22573 | 0.019 | 0.5939 | 0.3 | 12.2 | 0 | 0.31 | 1 | 1 | ol | TRUE | 0 | 0 | 0 | 0.00403 | 90 |  | 12895 | SWF | 0
12943 | 7097097_001001_001001_00100013_06001 | NYY 4x6 | 22056 | 17379 | 0.003 | 3.084 | 0.10085 | 0 | 0 | 0.056 | 1 | 1 | cs | TRUE | 12.336 | 0.40338 | 0 | 0.00393 | 70 |  | 12943 | SWF | 0
14065 | 7097097_001001_001001_00020003_06002 | NYY-J 3x70SM 0.6/1kV | 19999 | 23736 | 0.024 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 14065 | SWF | 0
14199 | 7097097_001001_001001_00120015_06001 | NS-Leitungstypen\15-AL1/3-ST1A 0.4 | 22092 | 20571 | 0.003 | 1.8769 | 0.35 | 11 | 0 | 0.105 | 1 | 1 | ol | TRUE | 0 | 0 | 0 | 0.00403 | 90 |  | 14199 | SWF | 0
14694 | 7097097_001001_001001_00080011_06001 | NS-Leitungstypen\15-AL1/3-ST1A 0.4 | 22097 | 13674 | 0.003 | 1.8769 | 0.35 | 11 | 0 | 0.105 | 1 | 1 | ol | TRUE | 0 | 0 | 0 | 0.00403 | 90 |  | 14694 | SWF | 0
15765 | 7097097_001001_001001_00140016_06002 | NS-Leitungstypen\15-AL1/3-ST1A 0.4 | 22562 | 17531 | 0.036 | 1.8769 | 0.35 | 11 | 0 | 0.105 | 1 | 1 | ol | TRUE | 0 | 0 | 0 | 0.00403 | 90 |  | 15765 | SWF | 0
15841 | 7097097_001001_001001_00090019_06001 | NAYY-J 4x50 | 20593 | 22572 | 0.024 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 15841 | SWF | 0
16005 | 7097097_001001_001001_00200023_06001 | NAYY-J 4x50 | 25593 | 25594 | 0.005 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 16005 | SWF | 0
16219 | 7097097_001001_001001_00050006_06001 | NYY 4x10 | 14276 | 25805 | 0.001 | 1.8303 | 0.094562 | 0 | 0 | 0.075 | 1 | 1 | cs | TRUE | 7.3214 | 0.37825 | 0 | 0.00393 | 70 |  | 16219 | SWF | 0
18196 | 7097097_001001_001001_00140017_06001 | NYY 4x6 | 22109 | 17645 | 0.003 | 3.084 | 0.10085 | 0 | 0 | 0.056 | 1 | 1 | cs | TRUE | 12.336 | 0.40338 | 0 | 0.00393 | 70 |  | 18196 | SWF | 0
19326 | 7097097_001001_001001_00180021_06002 | NAYY-J 4x50 | 22573 | 15603 | 0.014 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 19326 | SWF | 0
19872 | 7097097_001001_001001_00240025_06001 | NAYY-J 4x50 | 18541 | 29044 | 0.062 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 19872 | SWF | 0
20275 | 7097097_001001_001001_00200023_06002 | NAYY-J 4x50 | 17618 | 25593 | 0.009 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 20275 | SWF | 0
20510 | 7097097_001001_001001_00240026_06001 | NAYY 4x70SE 0.6/1kV | 29044 | 29590 | 0.023 | 0.4442 | 0.08231 | 750 | 0 | 0.176 | 1 | 1 | cs | TRUE | 1.7767 | 0.32924 | 312.4 | 0.00403 | 70 |  | 20510 | SWF | 0
21466 | 7097097_001001_001001_00180022_06001 | NS-Leitungstypen\15-AL1/3-ST1A 0.4 | 22102 | 15385 | 0.003 | 1.8769 | 0.35 | 11 | 0 | 0.105 | 1 | 1 | ol | TRUE | 0 | 0 | 0 | 0.00403 | 90 |  | 21466 | SWF | 0
22699 | 7097097_001001_001001_00020003_06001 | NAYY 4x95SE 0.6/1kV | 23736 | 21819 | 0.005 | 0.3208 | 0.081996 | 770 | 0 | 0.211 | 1 | 1 | cs | TRUE | 1.2833 | 0.32798 | 349.2 | 0.00403 | 70 |  | 22699 | SWF | 0
22723 | 7097097_001001_001001_00020004_06001 | NAYY-J 4x50 | 21819 | 19880 | 0.025 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 22723 | SWF | 0
25188 | 7097097_001001_001001_00090020_06001 | NAYBY 4x95sm 0.6/1kV | 22572 | 25594 | 0.013 | 0.3208 | 0.075398 | 840 | 0 | 0.21 | 1 | 1 | cs | TRUE | 1.2833 | 0.30159 | 404.3 | 0.00403 | 70 |  | 25188 | SWF | 0
25189 | 7097097_001001_001001_00200024_06001 | NAYBY 4x95sm 0.6/1kV | 25594 | 29044 | 0.033 | 0.3208 | 0.075398 | 840 | 0 | 0.21 | 1 | 1 | cs | TRUE | 1.2833 | 0.30159 | 404.3 | 0.00403 | 70 |  | 25189 | SWF | 0
29617 | 7097097_001001_001001_00010002_06002 | NAYY 4x185SE 0.6/1kV | 21819 | 33266 | 0.004 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 29617 | SWF | 0
32152 | 7097097_001001_001001_00020005_06001 | NAYY 4x150SE 0.6/1kV | 21819 | 25805 | 0.003 | 0.2067 | 0.080425 | 830 | 0 | 0.27 | 1 | 1 | cs | TRUE | 0.8267 | 0.3217 | 385.9 | 0.00403 | 70 |  | 32152 | SWF | 0
32153 | 7097097_001001_001001_00050007_06001 | NAYY 4x150SE 0.6/1kV | 25805 | 22548 | 0.005 | 0.2067 | 0.080425 | 830 | 0 | 0.27 | 1 | 1 | cs | TRUE | 0.8267 | 0.3217 | 385.9 | 0.00403 | 70 |  | 32153 | SWF | 0
33964 | 7097097_001001_001001_00010002_06001 | NS-Leitungstyp_fiktiv | 33266 | 22402 | 0.001 | 0.0001 | 0.0001 | 0 | 0 | 1 | 1 | 1 | cs | TRUE | 0 | 0 | 0 | 0.00403 | 80 |  | 33964 | SWF | 0

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service | vk0_percent | vkr0_percent | mag0_percent | mag0_rx | si0_hv_partial | tap_set_vm_pu | description | equipment
139 | 6097097_000000_000000_00000000_05001 | MSNS_1000 | 22401 | 22402 | 0.63 | 20 | 0.4 | 4.01 | 0.85714 | 0.6 | 0.3 | 150 | [6 empty] | 0 | FALSE | 1 | 1 | TRUE | 3 | 0 | 100 | 0 | 0.9 | 1

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
12841 | 11.0824 | 49.699 | 11.0823 | 49.6989 | 11.082 | 49.6986
12846 | 11.0811 | 49.698 | 11.0811 | 49.6977
12865 | 11.082 | 49.6986 | 11.082 | 49.6982 | 11.0821 | 49.6978
12866 | 11.0821 | 49.6978 | 11.0818 | 49.6979 | 11.0814 | 49.698
12867 | 11.0814 | 49.698 | 11.0811 | 49.698
12870 | 11.0808 | 49.6974 | 11.0811 | 49.6977
12893 | 11.082 | 49.6986 | 11.0816 | 49.6987
12894 | 11.0816 | 49.6987 | 11.0811 | 49.6987
12895 | 11.0811 | 49.6987 | 11.0808 | 49.6988
12943 | 11.0814 | 49.698 | 11.0814 | 49.698 | 11.0814 | 49.698
14065 | 11.0826 | 49.6989 | 11.0826 | 49.6989 | 11.0826 | 49.6989 | 11.0825 | 49.699 | 11.0823 | 49.699
14199 | 11.0811 | 49.698 | 11.0811 | 49.698 | 11.0811 | 49.698
14694 | 11.0821 | 49.6978 | 11.0821 | 49.6978 | 11.0821 | 49.6978
15765 | 11.0808 | 49.6974 | 11.0808 | 49.6974 | 11.0803 | 49.6974 | 11.0803 | 49.6974 | 11.0803 | 49.6974
15841 | 11.0817 | 49.6985 | 11.0817 | 49.6985 | 11.0817 | 49.6985 | 11.0817 | 49.6985 | 11.0817 | 49.6986 | 11.0816 | 49.6987
16005 | 11.0815 | 49.6986 | 11.0815 | 49.6986 | 11.0815 | 49.6986
16219 | 11.0824 | 49.699 | 11.0824 | 49.699
18196 | 11.0811 | 49.6977 | 11.0811 | 49.6977 | 11.0811 | 49.6977
19326 | 11.0808 | 49.6988 | 11.0808 | 49.6988 | 11.0808 | 49.6989 | 11.0808 | 49.6989 | 11.0808 | 49.6989
19872 | 11.0818 | 49.6981 | 11.0819 | 49.6982 | 11.0819 | 49.6982 | 11.0819 | 49.6982 | 11.0818 | 49.6982 | 11.0816 | 49.6983 | 11.0813 | 49.6983 | 11.0812 | 49.6984 | 11.0812 | 49.6984
20275 | 11.0814 | 49.6986 | 11.0814 | 49.6986 | 11.0814 | 49.6986 | 11.0815 | 49.6986 | 11.0815 | 49.6986 | 11.0815 | 49.6986
20510 | 11.0812 | 49.6984 | 11.0812 | 49.6984 | 11.0812 | 49.6984 | 11.0811 | 49.6983 | 11.0811 | 49.6984 | 11.081 | 49.6984 | 11.081 | 49.6984 | 11.081 | 49.6984 | 11.081 | 49.6983
21466 | 11.0811 | 49.6987 | 11.0811 | 49.6987 | 11.0811 | 49.6987
22699 | 11.0823 | 49.699 | 11.0824 | 49.699 | 11.0824 | 49.699
22723 | 11.0824 | 49.699 | 11.0824 | 49.699 | 11.0824 | 49.699 | 11.0825 | 49.699 | 11.0826 | 49.6989 | 11.0826 | 49.6989 | 11.0826 | 49.6989
25188 | 11.0816 | 49.6987 | 11.0816 | 49.6986 | 11.0816 | 49.6986 | 11.0815 | 49.6986
25189 | 11.0815 | 49.6986 | 11.0813 | 49.6984 | 11.0813 | 49.6984 | 11.0812 | 49.6984
29617 | 11.0824 | 49.699 | 11.0824 | 49.699 | 11.0824 | 49.699 | 11.0824 | 49.699 | 11.0824 | 49.699
32152 | 11.0824 | 49.699 | 11.0824 | 49.699 | 11.0824 | 49.699
32153 | 11.0824 | 49.699 | 11.0823 | 49.699 | 11.0824 | 49.699 | 11.0824 | 49.699
33964 | 11.0824 | 49.699 | 11.0824 | 49.699

## bus_geodata
| x | y | coords
22401 | 11.0824 | 49.699
22402 | 11.0824 | 49.699
22548 | 11.0824 | 49.699
22549 | 11.082 | 49.6986
29590 | 11.081 | 49.6983
15385 | 11.0811 | 49.6987
19999 | 11.0826 | 49.6989
22562 | 11.0808 | 49.6974
19880 | 11.0826 | 49.6989
22056 | 11.0814 | 49.698
22572 | 11.0816 | 49.6987
22573 | 11.0808 | 49.6988
23736 | 11.0823 | 49.699
21819 | 11.0824 | 49.699
14276 | 11.0824 | 49.699
22092 | 11.0811 | 49.698
25805 | 11.0824 | 49.699
22097 | 11.0821 | 49.6978
17618 | 11.0814 | 49.6986
22102 | 11.0811 | 49.6987
20571 | 11.0811 | 49.698
22109 | 11.0811 | 49.6977
17379 | 11.0814 | 49.698
13674 | 11.0821 | 49.6978
17645 | 11.0811 | 49.6977
18541 | 11.0818 | 49.6981
20593 | 11.0817 | 49.6985
33266 | 11.0824 | 49.699
15603 | 11.0808 | 49.6989
29044 | 11.0812 | 49.6984
25593 | 11.0815 | 49.6986
25594 | 11.0815 | 49.6986
17531 | 11.0803 | 49.6974

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | endtemp_degree | r0_ohm_per_km | x0_ohm_per_km | c0_nf_per_km
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
NS-Leitungstypen\15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
NYM 4x1.5 | 0 | 12.1187 | 0.10776 | 0.025 | cs | 0 | 0.00393 | 160 | 48.4747 | 0.43103 | 0
NYCWY 3x70/35 | 1120 | 0.26995 | 0.07477 | 0.227 | cs | 0 | 0.00393 | 160 | 1.0798 | 0.29908 | 672
NAYCWY 3x50/50 | 980 | 0.6417 | 0.077597 | 0.142 | cs | 0 | 0.00403 | 160 | 2.5668 | 0.31039 | 588
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
NAYBY 4x70sm 0.6/1kV | 810 | 0.4442 | 0.075398 | 0.175 | cs | 70 | 0.00403 | 160 | 1.7767 | 0.30159 | 367.6
NAYY 4x95SE 0.6/1kV | 770 | 0.3208 | 0.081996 | 0.211 | cs | 95 | 0.00403 | 160 | 1.2833 | 0.32798 | 349.2
NAYCWY 3x35/16 | 960 | 0.86558 | 0.078854 | 0.123 | cs | 0 | 0.00403 | 160 | 3.4623 | 0.31542 | 576
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
NYCWY 3x25/25 | 840 | 0.72796 | 0.080739 | 0.129 | cs | 0 | 0.00393 | 160 | 2.9118 | 0.32296 | 504
NYY-J 3x240SM 0.6/1kV | 1390 | 0.0777 | 0.072571 | 0.56 | cs | 240 | 0.00393 | 160 | 0.3106 | 0.29028 | 643.2
NKBA 4x95sm 0.6/1kV | 1000 | 0.1953 | 0.065973 | 0.28 | cs | 95 | 0.00393 | 180 | 0.7812 | 0.26389 | 514.6
NAYY 4x185SE 0.6/1kV | 830 | 0.165 | 0.080425 | 0.307 | cs | 185 | 0.00403 | 160 | 0.66 | 0.3217 | 385.9
NYY 4x10 | 0 | 1.8303 | 0.094562 | 0.075 | cs | 0 | 0.00393 | 160 | 7.3214 | 0.37825 | 0
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A_air | 12.6 | 0.413 | 0.29 | 0.31 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
NYY-J 4x16 | 0 | 1.1534 | 0.089535 | 0.098 | cs | 0 | 0.00393 | 160 | 4.6135 | 0.35814 | 0
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
NA2XS(F)2Y 1x150RM 12/20kV ir | 254 | 0.227 | 0.19541 | 0.353 | cs | 150 | 0.00403 | 250 | 0.832 | 0.309 | 253.6
NYY-O 3x120SM 0.6/1kV | 1309.9999 | 0.154 | 0.073199 | 0.309 | cs | 120 | 0.00393 | 160 | 0.6159 | 0.2928 | 569.7
NAYBY 4x150sm 0.6/1kV | 910 | 0.2075 | 0.072257 | 0.27 | cs | 150 | 0.00403 | 160 | 0.83 | 0.28903 | 441.1
NYY-J 4x25 | 0 | 0.72712 | 0.087965 | 0.129 | cs | 0 | 0.00393 | 160 | 2.9085 | 0.35186 | 0
NYCWY 3x16/16 | 800 | 1.1534 | 0.08231 | 0.099 | cs | 0 | 0.00393 | 160 | 4.6135 | 0.32924 | 480
NYCWY 3x35/35 | 960 | 0.52486 | 0.077912 | 0.156 | cs | 0 | 0.00393 | 160 | 2.0995 | 0.31165 | 576
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NAYY 4x70SE 0.6/1kV | 750 | 0.4442 | 0.08231 | 0.176 | cs | 70 | 0.00403 | 160 | 1.7767 | 0.32924 | 312.4
NYY-O 3x70SM 0.6/1kV | 1130 | 0.2686 | 0.07477 | 0.225 | cs | 70 | 0.00393 | 160 | 1.0745 | 0.29908 | 477.8
NA2XS(F)2Y 1x240RM 12/20kV ir | 304 | 0.144 | 0.18253 | 0.456 | cs | 240 | 0.00403 | 250 | 0.749 | 0.303 | 303.2
NA2XS2Y 1x240RM 12/20kV ir | 304 | 0.144 | 0.18253 | 0.456 | cs | 240 | 0.00403 | 250 | 0.749 | 0.303 | 303.2
NEKBA 3x70rm 12/20kV | 280 | 0.2705 | 0.11624 | 0.22 | cs | 70 | 0.00393 | 155 | 1.0821 | 0.46496 | 284.9
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
15-AL1/3-ST1A 0.4_air | 11 | 1.8769 | 0.35 | 0.31 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
NAEKBA 3x95rm 12/20kV | 310 | 0.3203 | 0.10996 | 0.21 | cs | 95 | 0.00403 | 155 | 1.2814 | 0.43982 | 314.3
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
NYCWY 3x95/95 | 1160 | 0.19473 | 0.07477 | 0.272 | cs | 0 | 0.00393 | 160 | 0.77894 | 0.29908 | 696
NYY-J 3x70SM 0.6/1kV | 1130 | 0.2686 | 0.07477 | 0.276 | cs | 70 | 0.00393 | 160 | 1.0745 | 0.29908 | 477.8
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
N2XS(F)2Y 1x300RM/25 12/20kV it | 329 | 0.065 | 0.10996 | 0.597 | cs | 300 | 0.00393 | 250 | 0.2599 | 0.43982 | 328
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
NA2XS(F)2Y 1x95RM 12/20kV ir | 216 | 0.334 | 0.20986 | 0.282 | cs | 95 | 0.00403 | 250 | 1.134 | 0.563 | 215
NA2XS2Y 1x120RM 12/20kV ir | 235 | 0.267 | 0.20326 | 0.32 | cs | 120 | 0.00403 | 250 | 1.065 | 0.56 | 234.3
48-AL1/8-ST1A 0.4_air | 12.2 | 0.5939 | 0.3 | 0.31 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NAEKBA 3x120rm 12/20kV | 350 | 0.2534 | 0.10681 | 0.235 | cs | 120 | 0.00403 | 155 | 1.0136 | 0.42726 | 346.4
NA2YSY 1x150rm 12/20kV ir | 260 | 0.2092 | 0.11624 | 0.325 | cs | 150 | 0.00403 | 150 | 0.8367 | 0.46496 | 275.7
NKBA 4x70sm 0.6/1kV | 880 | 0.2707 | 0.069115 | 0.235 | cs | 70 | 0.00393 | 180 | 1.0827 | 0.27646 | 441.1
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
NKBA 4x120sm 0.6/1kV | 1140 | 0.1556 | 0.065973 | 0.32 | cs | 120 | 0.00393 | 180 | 0.6224 | 0.26389 | 606.5
NYY-J 4x35 | 0 | 0.52403 | 0.085137 | 0.156 | cs | 0 | 0.00393 | 160 | 2.0961 | 0.34055 | 0
NYM 4x50 | 0 | 0.38696 | 0.084823 | 0.185 | cs | 0 | 0.00393 | 160 | 1.5478 | 0.33929 | 0
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
NYY-J 3x95SM 0.6/1kV | 1160 | 0.1941 | 0.07477 | 0.332 | cs | 95 | 0.00393 | 160 | 0.7766 | 0.29908 | 496.2
NYCY 4x16/16 | 800 | 1.15 | 0.089535 | 0.102 | cs | 0 | 0.00393 | 160 | 4.6 | 0.35814 | 480
NAYY-J 4x35 | 0 | 0.869 | 0.085137 | 0.123 | cs | 0 | 0 | 160 | 3.476 | 0.34055 | 0
NA2YSY 1x95rm 12/20kV ir | 230 | 0.3225 | 0.12566 | 0.265 | cs | 95 | 0.00403 | 150 | 1.29 | 0.50265 | 238.9
NYY-J 4x50 | 0 | 0.38696 | 0.084823 | 0.185 | cs | 0 | 0.00393 | 160 | 1.5478 | 0.33929 | 0
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
NAYBY 4x50sm 0.6/1kV | 710 | 0.6417 | 0.07854 | 0.14 | cs | 50 | 0.00403 | 160 | 2.5667 | 0.31416 | 312.4
NYY-O 3x240SM 0.6/1kV | 1390 | 0.0777 | 0.072571 | 0.458 | cs | 240 | 0.00393 | 160 | 0.3106 | 0.29028 | 643.2
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
NYY-O 3x150SM 0.6/1kV | 1320.0001 | 0.1255 | 0.073199 | 0.348 | cs | 150 | 0.00393 | 160 | 0.5021 | 0.2928 | 588.1
N2XS(F)2Y 1x400RM/35 12/20kV it | 368 | 0.0535 | 0.11153 | 0.671 | cs | 400 | 0.00393 | 250 | 0.214 | 0.44611 | 366.6
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
94-AL1/15-ST1A 0.4_air | 13.2 | 0.306 | 0.29 | 0.31 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
NYY-J 3x150SM 0.6/1kV | 1320.0001 | 0.1255 | 0.073199 | 0.426 | cs | 150 | 0.00393 | 160 | 0.5021 | 0.2928 | 588.1
NAYCWY 3x120/120 | 1280 | 0.3221 | 0.073199 | 0.24 | cs | 0 | 0.00403 | 160 | 1.2884 | 0.2928 | 768
NYCWY 3x50/50 | 980 | 0.3878 | 0.077597 | 0.184 | cs | 0 | 0.00393 | 160 | 1.5512 | 0.31039 | 588
NAYY-J 3x35/35 | 0 | 0.869 | 0.085137 | 0.123 | cs | 0 | 0 | 160 | 3.476 | 0.34055 | 0
NYCWY 3x95/50 | 1160 | 0.19473 | 0.07477 | 0.272 | cs | 0 | 0.00393 | 160 | 0.77894 | 0.29908 | 696
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
24-AL1/4-ST1A 0.4_air | 11.25 | 1.2012 | 0.335 | 0.31 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
NAYY 4x150SE 0.6/1kV | 830 | 0.2067 | 0.080425 | 0.27 | cs | 150 | 0.00403 | 160 | 0.8267 | 0.3217 | 385.9
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
NAYY 4x120SE 0.6/1kV | 840 | 0.2542 | 0.080425 | 0.24 | cs | 120 | 0.00403 | 160 | 1.0167 | 0.3217 | 385.9
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
NAEKBA 3x50rm 12/20kV | 240 | 0.6415 | 0.12252 | 0.14 | cs | 50 | 0.00403 | 155 | 2.5661 | 0.49009 | 248.1
NEKBA 3x50rm 12/20kV | 240 | 0.3913 | 0.12252 | 0.18 | cs | 50 | 0.00393 | 155 | 1.5653 | 0.49009 | 248.1
N2YSY 1x70rm 12/20kV ir | 200 | 0.2711 | 0.13195 | 0.285 | cs | 70 | 0.00393 | 150 | 1.0845 | 0.52779 | 211.3
MS-Leitungstyp_fiktiv | 0 | 0 | 0 | 1 | cs | 0 | 0.00403 | 80 | 0 | 0 | 0
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
NAYY-J 4x50 | 0 | 0.641 | 0.084823 | 0.144 | cs | 0 | 0 | 160 | 2.564 | 0.33929 | 0
NA2YSY 1x240rm 12/20kV ir | 310 | 0.1292 | 0.10996 | 0.425 | cs | 240 | 0.00403 | 150 | 0.5167 | 0.43982 | 321.6
NAYY 4x240SE 0.6/1kV | 870 | 0.1267 | 0.079796 | 0.357 | cs | 240 | 0.00403 | 160 | 0.5067 | 0.31919 | 422.7
NYCWY 3x25/16 | 840 | 0.72796 | 0.080739 | 0.129 | cs | 0 | 0.00393 | 160 | 2.9118 | 0.32296 | 504
NEKBA 3x95rm 12/20kV | 310 | 0.1948 | 0.10996 | 0.27 | cs | 95 | 0.00393 | 155 | 0.7792 | 0.43982 | 314.3
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
NAEKBA 3x150rm 12/20kV | 370 | 0.2076 | 0.10367 | 0.265 | cs | 150 | 0.00403 | 155 | 0.8305 | 0.41469 | 374
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NAYY 1x240RM 0.6/1kV ir | 800 | 0.1258 | 0.17719 | 0.432 | cs | 240 | 0.00403 | 160 | 0.5033 | 0.70874 | 808.6
MS/FL-Al/St 95/15 (410107)_air | 10 | 0.304 | 0.373 | 1 | ol | 0 | 0.00403 | 80 | 0.452 | 1.464 | 4
NAYBY 4x95sm 0.6/1kV | 840 | 0.3208 | 0.075398 | 0.21 | cs | 95 | 0.00403 | 160 | 1.2833 | 0.30159 | 404.3
NKBA 0.6/1 kV 3x50/ 25sm | 680 | 0.387 | 0.087996 | 0.191 | cs | 50 | 0.00393 | 180 | 1.548 | 0.35198 | 408
NYY 4x6 | 0 | 3.084 | 0.10085 | 0.056 | cs | 0 | 0.00393 | 160 | 12.336 | 0.40338 | 0
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
NYY-J 4x120 | 0 | 0.15378 | 0.080425 | 0.313 | cs | 0 | 0.00393 | 160 | 0.61513 | 0.3217 | 0
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NKBA 0.6/1 kV 3x35/ 16sm | 590 | 0.524 | 0.090981 | 0.161 | cs | 35 | 0.00393 | 180 | 2.096 | 0.36392 | 354
NYY 4x1.5 | 0 | 12.1187 | 0.11498 | 0.026 | cs | 0 | 0.00393 | 160 | 48.4747 | 0.45993 | 0
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
NKBA 4x50sm 0.6/1kV | 760 | 0.3914 | 0.069115 | 0.19 | cs | 50 | 0.00393 | 180 | 1.5656 | 0.27646 | 349.2
NS-Leitungstyp_fiktiv | 0 | 0 | 0 | 1 | cs | 0 | 0.00403 | 80 | 0 | 0 | 0
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
NYCWY 3x70/70 | 1120 | 0.26995 | 0.07477 | 0.227 | cs | 0 | 0.00393 | 160 | 1.0798 | 0.29908 | 672
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
NYY-J 3x185SM 0.6/1kV | 1320.0001 | 0.1013 | 0.073199 | 0.483 | cs | 185 | 0.00393 | 160 | 0.405 | 0.2928 | 588.1
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
NAYCWY 3x35/35 | 960 | 0.86558 | 0.078854 | 0.123 | cs | 0 | 0.00403 | 160 | 3.4623 | 0.31542 | 576
NYY 4x2.5 | 0 | 7.4133 | 0.10681 | 0.034 | cs | 0 | 0.00393 | 160 | 29.6532 | 0.42726 | 0
NYCWY 4x35/16 | 960 | 0.52486 | 0.085137 | 0.157 | cs | 0 | 0.00393 | 160 | 2.0995 | 0.34055 | 576
NKBA 4x35sm 0.6/1kV | 590 | 0.524 | 0.091012 | 0.161 | cs | 35 | 0.00393 | 180 | 2.096 | 0.36405 | 590
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
NYY 4x4 | 0 | 4.6135 | 0.1065 | 0.044 | cs | 0 | 0.00393 | 160 | 18.4538 | 0.426 | 0
NA2XY 3x150sm 0.6/1kV | 610 | 0.207 | 0.069115 | 0.3 | cs | 150 | 0.00403 | 250 | 0.8281 | 0.27646 | 238.9
NYY 3x1.5 | 0 | 12.1187 | 0.10776 | 0.025 | cs | 0 | 0.00393 | 160 | 48.4747 | 0.43103 | 0

## trafo_std_types
| sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | vector_group | vk0_percent | vkr0_percent | mag0_percent | mag0_rx | si0_hv_partial | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
MSNS_0126 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0062 | 0.4 | 20 | 0.4 | 4.16 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0008 | 0.63 | 20 | 0.4 | 4.04 | 0.7627 | 0.556 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0138 | 0.63 | 20 | 0.4 | 4 | 0.83937 | 0.542 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0150 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0141 | 0.63 | 20 | 0.4 | 4.1 | 0.83063 | 0.819 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0089 | 0.4 | 20 | 0.4 | 3.74 | 1.35 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0060 | 0.4 | 20 | 0.4 | 3.825 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0091 | 0.4 | 20 | 0.4 | 3.87 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0087 | 0.4 | 20 | 0.4 | 3.98 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0163 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0059 | 0.8 | 20 | 0.4 | 4.2 | 0.875 | 0.8 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0080 | 0.63 | 20 | 0.4 | 4.1 | 0.85937 | 0.589 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0153 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0148 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0140 | 0.63 | 20 | 0.4 | 4.1 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0061 | 0.63 | 20 | 0.4 | 3.9 | 0.71 | 0.562 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0077 | 0.315 | 20 | 0.4 | 3.89 | 0.98413 | 0.35 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0039 | 0.4 | 20 | 0.4 | 3.8 | 1.35 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0161 | 0.63 | 20 | 0.4 | 4.25 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0017 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0011 | 0.4 | 20 | 0.4 | 4.14 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0040 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0121 | 0.515 | 20 | 0.4 | 4.1 | 0.93204 | 0.515 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0051 | 0.63 | 20 | 0.4 | 4.11 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
160 MVA 380/110 kV | 160 | 380 | 110 | 12.2 | 0.25 | 60 | 0.06 | 0 | Yy0 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0
MSNS_0137 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0004 | 0.4 | 20 | 0.4 | 4.01 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0093 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0147 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0013 | 0.515 | 20 | 0.4 | 4 | 0.93204 | 0.515 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0172 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0046 | 0.4 | 20 | 0.4 | 3.85 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0021 | 0.4 | 20 | 0.4 | 3.8 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0124 | 0.63 | 20 | 0.4 | 3.7 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0102 | 0.315 | 20 | 0.4 | 3.95 | 0.98413 | 0.35 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0018 | 0.4 | 20 | 0.4 | 4.25 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0107 | 0.63 | 20 | 0.4 | 4.05 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0164 | 0.4 | 20 | 0.4 | 3.81 | 0.75125 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0005 | 0.63 | 20 | 0.4 | 4.15 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0135 | 0.63 | 20 | 0.4 | 3.94 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0035 | 0.63 | 20 | 0.4 | 4 | 0.84317 | 0.566 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0181 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0073 | 0.4 | 20 | 0.4 | 3.9 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0123 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0067 | 0.4 | 20 | 0.4 | 4.13 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0167 | 0.63 | 20 | 0.4 | 4.04 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0081 | 0.63 | 20 | 0.4 | 4.1 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.25 MVA 10/0.4 kV | 0.25 | 10 | 0.4 | 4 | 1.2 | 0.6 | 0.24 | 150 | Dyn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | 0
MSNS_0086 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0195 | 0.63 | 20 | 0.4 | 4.01 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0149 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0128 | 0.63 | 20 | 0.4 | 4.15 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0146 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0047 | 0.63 | 20 | 0.4 | 4.3 | 0.85714 | 0.6 | 0.3 | 150 | Dy5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0106 | 0.63 | 20 | 0.4 | 3.95 | 0.78238 | 0.5945 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0015 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0198 | 0.515 | 20 | 0.4 | 3.9 | 1.0485 | 0.30191 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.25 MVA 20/0.4 kV | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | Yzn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | 0
MSNS_0025 | 0.4 | 20 | 0.4 | 3.81 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0029 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0160 | 0.315 | 20 | 0.4 | 4 | 0.98413 | 0.35 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
40 MVA 110/10 kV | 40 | 110 | 10 | 16.2 | 0.34 | 18 | 0.05 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0
MSNS_0054 | 0.2 | 20 | 0.4 | 4.22 | 1 | 0.2 | 0.3 | 150 | Yz5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0129 | 0.63 | 20 | 0.4 | 4.2 | 0.83238 | 0.581 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.63 MVA 20/0.4 kV | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | Dyn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | 0
MSNS_0076 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dy5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0068 | 0.63 | 20 | 0.4 | 4.4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.4 MVA 20/0.4 kV | 0.4 | 20 | 0.4 | 6 | 1.425 | 1.35 | 0.3375 | 150 | Dyn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | 0
MSNS_0194 | 0.63 | 20 | 0.4 | 4.2 | 0.81079 | 0.546 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0042 | 0.63 | 20 | 0.4 | 4.4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0053 | 0.63 | 20 | 0.4 | 4.05 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0056 | 0.2 | 20 | 0.4 | 3.86 | 1 | 0.2 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0078 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0098 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0069 | 0.63 | 20 | 0.4 | 4.4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0101 | 0.63 | 20 | 0.4 | 4 | 0.71127 | 0.588 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0085 | 0.4 | 20 | 0.4 | 3.87 | 0.7625 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_1000 | 0.63 | 20 | 0.4 | 4.01 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0057 | 0.4 | 20 | 0.4 | 4.88 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.4 MVA 10/0.4 kV | 0.4 | 10 | 0.4 | 4 | 1.325 | 0.95 | 0.2375 | 150 | Dyn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | 0
MSNS_0063 | 0.4 | 20 | 0.4 | 3.81 | 0.9605 | 0.397 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
OR 40000/110 27332688 | 40 | 115.1 | 21 | 13.92 | 0.38255 | 19.613 | 0.05 | 150 | YNd5 | 0 | 0 | 100 | 0 | 0.9
63 MVA 110/20 kV | 63 | 110 | 20 | 18 | 0.32 | 22 | 0.04 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0
MSNS_0156 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0009 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0142 | 0.2 | 20 | 0.4 | 4 | 1.15 | 0.22 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0044 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0028 | 0.63 | 20 | 0.4 | 4.01 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0131 | 0.63 | 20 | 0.4 | 3.9 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0012 | 0.63 | 20 | 0.4 | 6 | 0.0011111 | 0.00099 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0108 | 0.4 | 20 | 0.4 | 4.2 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0092 | 0.4 | 20 | 0.4 | 3.54 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0050 | 0.4 | 20 | 0.4 | 4.2 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0158 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
25 MVA 110/10 kV | 25 | 110 | 10 | 12 | 0.41 | 14 | 0.07 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0
MSNS_0185 | 0.63 | 20 | 0.4 | 3.89 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0058 | 0.515 | 20 | 0.4 | 4.025 | 0.87039 | 0.475 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0041 | 0.4 | 20 | 0.4 | 4.5 | 1.35 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0003 | 0.715 | 20 | 0.4 | 4.1 | 0.86713 | 0.7 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0162 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0034 | 0.63 | 20 | 0.4 | 3.82 | 0.00063492 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0192 | 0.63 | 20 | 0.4 | 4.16 | 0.76651 | 0.552 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0043 | 0.4 | 20 | 0.4 | 4.27 | 0.75125 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0191 | 0.63 | 20 | 0.4 | 3.98 | 0.45984 | 0.523 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.63 MVA 10/0.4 kV | 0.63 | 10 | 0.4 | 4 | 1.0794 | 1.18 | 0.1873 | 150 | Dyn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | 0
MSNS_0113 | 0.4 | 20 | 0.4 | 4.1 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0133 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0196 | 0.4 | 20 | 0.4 | 3.79 | 0.75125 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0109 | 0.63 | 20 | 0.4 | 4.1 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0097 | 0.63 | 20 | 0.4 | 4.15 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0104 | 0.4 | 20 | 0.4 | 4.05 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0014 | 0.4 | 20 | 0.4 | 3.9 | 0.6575 | 0.407 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0145 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0136 | 0.63 | 20 | 0.4 | 4.1 | 0.84317 | 0.844 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0175 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0036 | 0.4 | 20 | 0.4 | 3.75 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0001 | 0.63 | 20 | 0.4 | 4.05 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0020 | 0.63 | 20 | 0.4 | 4.05 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0052 | 0.63 | 20 | 0.4 | 4.05 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0019 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0079 | 0.4 | 20 | 0.4 | 3.8 | 0.75125 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0168 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0169 | 0.25 | 20 | 0.4 | 3.8 | 0.35 | 0.09 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
25 MVA 110/20 kV | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0
MSNS_0165 | 0.63 | 20 | 0.4 | 4.03 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0032 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0072 | 0.4 | 20 | 0.4 | 3.65 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0030 | 0.8 | 20 | 0.4 | 4.2 | 0.875 | 0.8 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0199 | 0.63 | 20 | 0.4 | 4.065 | 0.97048 | 0.784 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0177 | 0.63 | 20 | 0.4 | 3.77 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0120 | 0.4 | 20 | 0.4 | 4.45 | 1.2 | 0.515 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0016 | 0.4 | 20 | 0.4 | 3.48 | 1.05 | 0.43 | 0.3 | 150 | Dy5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0088 | 0.515 | 20 | 0.4 | 4 | 0.93204 | 0.515 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0045 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0048 | 0.4 | 20 | 0.4 | 3.79 | 1.35 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0037 | 0.63 | 20 | 0.4 | 4.1 | 0.85714 | 0.6 | 0.3 | 150 | Dy5 | 3 | 0 | 100 | 0 | 0.9
40 MVA 110/20 kV | 40 | 110 | 20 | 16.2 | 0.34 | 18 | 0.05 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0
63 MVA 110/10 kV | 63 | 110 | 10 | 18 | 0.32 | 22 | 0.04 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0
MSNS_0103 | 0.4 | 20 | 0.4 | 3.65 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0112 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0186 | 0.63 | 20 | 0.4 | 3.9 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0074 | 0.4 | 20 | 0.4 | 4.1 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0170 | 0.63 | 20 | 0.4 | 4.12 | 0.77762 | 0.567 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
100 MVA 220/110 kV | 100 | 220 | 110 | 12 | 0.26 | 55 | 0.06 | 0 | Yy0 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | bus | description | object
6 | bus | substat | object
7 | bus | folder_id | object
8 | bus | sernum | object
9 | bus | for_name | object
10 | bus | chr_name | object
11 | load | name | object
12 | load | bus | uint32
13 | load | p_mw | float64
14 | load | q_mvar | float64
15 | load | const_z_percent | float64
16 | load | const_i_percent | float64
17 | load | sn_mva | float64
18 | load | scaling | float64
19 | load | in_service | bool
20 | load | type | object
21 | load | description | object
22 | load | sernum | object
23 | load | for_name | object
24 | load | chr_name | object
25 | sgen | name | object
26 | sgen | bus | int64
27 | sgen | p_mw | float64
28 | sgen | q_mvar | float64
29 | sgen | sn_mva | float64
30 | sgen | scaling | float64
31 | sgen | in_service | bool
32 | sgen | type | object
33 | sgen | current_source | bool
34 | sgen | description | object
35 | switch | bus | int64
36 | switch | element | int64
37 | switch | et | object
38 | switch | type | object
39 | switch | closed | bool
40 | switch | name | object
41 | switch | z_ohm | float64
42 | switch | in_ka | float64
43 | ext_grid | name | object
44 | ext_grid | bus | uint32
45 | ext_grid | vm_pu | float64
46 | ext_grid | va_degree | float64
47 | ext_grid | slack_weight | float64
48 | ext_grid | in_service | bool
49 | ext_grid | s_sc_max_mva | float64
50 | ext_grid | s_sc_min_mva | float64
51 | ext_grid | rx_min | float64
52 | ext_grid | rx_max | float64
53 | ext_grid | r0x0_max | float64
54 | ext_grid | x0x_max | float64
55 | ext_grid | r0x0_min | float64
56 | ext_grid | x0x_min | float64
57 | ext_grid | description | object
58 | line | name | object
59 | line | std_type | object
60 | line | from_bus | uint32
61 | line | to_bus | uint32
62 | line | length_km | float64
63 | line | r_ohm_per_km | float64
64 | line | x_ohm_per_km | float64
65 | line | c_nf_per_km | float64
66 | line | g_us_per_km | float64
67 | line | max_i_ka | float64
68 | line | df | float64
69 | line | parallel | uint32
70 | line | type | object
71 | line | in_service | bool
72 | line | r0_ohm_per_km | float64
73 | line | x0_ohm_per_km | float64
74 | line | c0_nf_per_km | float64
75 | line | alpha | float64
76 | line | temperature_degree_celsius | float64
77 | line | description | object
78 | line | line_idx | float64
79 | line | folder_id | object
80 | line | section_idx | int64
81 | trafo | name | object
82 | trafo | std_type | object
83 | trafo | hv_bus | uint32
84 | trafo | lv_bus | uint32
85 | trafo | sn_mva | float64
86 | trafo | vn_hv_kv | float64
87 | trafo | vn_lv_kv | float64
88 | trafo | vk_percent | float64
89 | trafo | vkr_percent | float64
90 | trafo | pfe_kw | float64
91 | trafo | i0_percent | float64
92 | trafo | shift_degree | float64
93 | trafo | tap_side | object
94 | trafo | tap_neutral | float64
95 | trafo | tap_min | float64
96 | trafo | tap_max | float64
97 | trafo | tap_step_percent | float64
98 | trafo | tap_step_degree | float64
99 | trafo | tap_pos | int32
100 | trafo | tap_phase_shifter | bool
101 | trafo | parallel | uint32
102 | trafo | df | float64
103 | trafo | in_service | bool
104 | trafo | vk0_percent | float64
105 | trafo | vkr0_percent | float64
106 | trafo | mag0_percent | float64
107 | trafo | mag0_rx | float64
108 | trafo | si0_hv_partial | float64
109 | trafo | tap_set_vm_pu | float64
110 | trafo | description | object
111 | trafo | equipment | object
112 | line_geodata | coords | object
113 | bus_geodata | x | float64
114 | bus_geodata | y | float64
115 | bus_geodata | coords | object

## parameters
| version | format_version | OPF_converged | name
0 | 2.13.1 | 2.12.0 | FALSE | Gesamtnetz